| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 1. | Pre-treatment |  |  |  |
| 1.1. | Screens |  |  |  |
| 1.2. | Settling chamber | Gas poisoning due to presence of H2S | - Check presence of gas and , if required, ventilate settling chamber/pit before entering - Person entering pit to be secured with life line, loose end held by person outside the pit | - lead acetate paper or H2S detection instrument - life line and belt - first aid kit including Amyl Nitrite capsule |
| 2. | Collection system |  |  |  |
| 2.1. | Pipelines | Injuries during excavation and repair work | - Clearly mark excavation area with cautionary sign boards (e.g. “man at work”) - Assign CETP engineer to supervise, if carried out by contractor | - marker, barriers, flags, boards |
| - 2.2. | Man-holes | Gas poisoning due to presence of H2S | Preferably, procure man-hole cleaning equipment to avoid entering of workers into man-holes at all - Check presence of gas and, if required, ventilate man hole before entering - Person entering to be secured with life line, loose end held by person outside the man hole - Person always to wear mask connected to air supply system | - Lead acetate paper or H2S detection instrument - Life line and belt - Air supply system - Separate first aid kit (including Amyl Nitrite capsule) to be part of collection maintenance kit |
|  |  | Injuries due to falls in open and unguarded man-holes | - Ensure proper cover of man-holes - Secure open man-holes while work on-going | - markers, barriers, flags |
|  |  | Suffocation die to small man-hole diameter | - Proper design and installation of man-holes as per regulations (at least 60 millimeter diameter) |  |
| 2.3. | Pumps | Electrocution due to loose wires, open connections, missing and improper earthing | - Work to be carried out by qualified (licensed) contractors - Regular checks of installations and equipment | - insulation mats |
|  |  | Injuries during repair work due to improper lifting of pumps as well as due unguarded pump parts | - Check technical specifications an maintenance of lifting device - Person to keep clear of load while lifting - Guards on pump drives to be kept in place |  |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 3. | CETP/ETP |  |  |  |
| 3.1. | Receiving sump and screen chamber |  | Preferably, entering of workers into man-holes to be avoided at all. Installation of mechanical screens instead of manual cleaning to be considered. |  |
|  |  | Gas poisoning due to presence of H2S | - Check presence of gas and, if required, ventilate chamber before entering - Person entering to be secured with life line, loose end held by person outside the man hole - Person always to wear mask connected to air supply system | - lead acetate paper or H2S detection instrument - life line and belt - air supply system |
|  |  | Skin diseases due to exposure of skins and body parts during cleaning/maintenance work | - Use equipment such as rake and shovels - Provide and use personal protective equipment (gloves, footwear, full body apron or full body PVC suit - Wash after completion of work at screen chamber | - rakes with long handles - personal protective equipment |
|  |  | Injuries and drowning due to falls/slips into unguarded receiving sumps/pits | - Provide cover or fence type railing around and ensure these are in place all the time - Provide rescuing equipment next to receiving area (location marked) | - life buoy with life line |
| - 3.2. | Equalisation tank | Injuries and drowning due to falls/slips into unguarded tanks | - Provide fence type railings and toe rails for all walk ways and platforms - Ensure these are in place all the time and not corroded - Provide rescuing equipment on platform (location marked) | - life buoy with life line |
|  |  | Injuries during repair work due to improper lifting of aerators, etc. | - Check technical specifications an maintenance of lifting device - Person to keep clear of load while lifting - Persons entering ET die fix rope/chain to be secured with life-line | - safety harness and life line - personal protective equipment (helmet, gloves) |
|  |  | Electrocution due to loose wires, open connections, improper and missing earthing | - Adequate wiring and electrical installation suitable for corrosive conditions (due to H2S). - Frequently check connections and conditions of wires and, if required, replace immediately | - use starter boxes made of plastic - use fully covered earthing wires - install circuit breakers and not fuses |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 3.3. | Chemical treatment: (a) Flash mixer | Skin burns, eye irritation due to spillage of chemicals (unhydrated lime, acidic alum solution) | - Installation of mechanical dosing system - Keep clear from chemical slurry while being added - Worker to wear personal protective equipment such as gloves, goggles, while mixing, dosing or monitoring | - personal protective equipment |
|  | (b) Clariflocculator | Injuries and drowning due to falls/slips into unguarded tanks | - Provide fence type railings and toe rails for all walk ways and platforms - Ensure these are in place all the time and not corroded - Provide rescuing equipment on platform (location marked) | - life buoy with life line |
|  |  | Injuries due to unguarded drive and gears of mechanical parts | - Provide covers for moving machine parts - Guard approach to gears (gear box, reduction gear, prime mover) |  |
|  |  | Electrocution due to loose wires, open connections, improper and missing earthing | - Adequate wiring and electrical installation suitable for corrosive conditions. - Frequently check connections and conditions of wires and, if required, replace immediately |  |
| 3.4. | Biological treatment | Injuries and drowning due to falls/slips into unguarded tanks | - Provide fence type railings (protected against corrosion) and toe rails for all walk ways and platforms - Ensure these are in place all the time and not corroded - Provide rescuing equipment on platform (location marked) | - life buoy with life line |
|  |  | Respiratory problems due to aerosols/foams | - Ensure proper submergence of aerators - Ensure proper free board in tanks - Control foam by spray water jets and anti-foaming agents - Do not assign workers showing allergic reactions to aerosols - Provide masks (suitable against organic vapours/aerosols) to workers - Affix cautionary sign “use personal protective equipment” | - water jet system - personal protective equipment |
|  |  | Injuries due to slippery walkways caused by spillage/foam | - Provide for adequate free board - Control foam by spray water jets - Frequently flush walkways - Affix cautionary sign “slippery floor” |  |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 3.4. | contn. | Injuries due to unguarded drive and gears of mechanical parts | - Provide covers for moving machine parts - Guard approach to gears (gear box, reduction gear, prime mover) |  |
|  |  | Electrocution due to loose wires, open connections, improper and missing earthing | - Adequate wiring and electrical installation suitable for corrosive conditions. - Frequently check connections and conditions of wires and, if required, replace immediately |  |
| 3.5. | Pipeline and pumping (valves chambers, pipes) | Injuries due to falls/slips into unguarded openings | - Provide covers on all openings or fence adequately |  |
|  |  | Suffocation in valve chambers due to lack of oxygen | - Provide spindles for manually operate valve chambers - Ensure adequate size valve chambers for maintenance work - Properly ventilate valve chamber before entering |  |
| 3.6. | Sludge management |  |  |  |
|  | (a) Sludge thickener | Injuries and drowning due to falls/slips into unguarded tanks | - Provide fence type railings and toe rails for all walk ways and platforms - Ensure these are in place all the time and not corroded - Restrict admission to platforms - Provide rescuing equipment on platform (location marked) | - life buoy with life line |
|  |  | Injuries due to unguarded drive and gears of mechanical parts | - Provide covers for moving machine parts - Guard approach to gears (gear box, reduction gear, prime mover) |  |
|  |  | Electrocution due to loose wires, open connections, improper and missing earthing | - Adequate wiring and electrical installation suitable for corrosive conditions. - Frequently check connections and conditions of wires and, if required, replace immediately |  |
|  | (b) Mechanical dewatering equipment | Injuries due to unguarded machine parts | - Provide covers for moving machine parts - Guard approach to gears (gear box, reduction gear, prime mover) |  |
|  |  | Electrocution due to loose wires, open connections, improper and missing earthing | - Adequate wiring and electrical installation suitable for corrosive conditions. - Frequently check connections and conditions of wires and, if required, replace immediately |  |
|  |  | Hearing impairment due to noise generation | - Provide hearing protection to machine operators | - personal protective equipment |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 3.6. | c) Sludge handling | Skin ailments due to chemicals present in sludge | - Consider mechanical handling as far as possible - Provide adequate protective equipment to workers - If done by contractor, ensure workers are provided with personal protective equipment | - personal protective equipment |
| - 4. | Chemical management |  |  |  |
| 4.1. | Chemical storage | Respiratory diseases and skin diseases due (chemical dust) | - Arrange supply of lime powder in canvas bags - Install and maintain proper ventilation in chemical store - Provide dust mask and goggles to workers engaged in handling lime powder bags - Provide personal protective equipment to workers handling acidic alum solutions - Affix appropriate warning sign “ use personal protective equipment” | - personal protective equipment |
| - 4.2. | Chemical preparation and dosing | Skin burns and irritation of eyes due to lime spillage | - If feasible, provide closed dosing system. - Provide tools for handling of chemicals - Provide personal protective equipment to workers | - handling tools - personal protective equipment |
|  |  | Respiratory diseases and skin diseases | - Install and maintain proper ventilation in chemical store - Reduce exposure time of workers in chemical dosing area - Provide personal protective equipment to workers - Affix appropriate warning sign “use personal protective equipment” | - personal protective equipment |
|  |  | Injuries from falls/slips due to slippery floor conditions | - Prevent leakage from dosing pumps and pillage from mixing tanks - Install drainage around mixing units - Ensure regular flushing and washing of floors - Install non-slippery and sloped flooring |  |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 5. | Laboratory | Skin burns/eye irritation to due to laboratory chemicals | - Always use personal protective laboratory equipment - Visibly display laboratory safety regulations and ensure proper labelling of all chemicals - Restrict admission to laboratory to authorised persons only - Provide separate training to all persons engaged in laboratory - Display boards explaining first aid and other emergency measures - Keep special emergency equipment ready (eye and skin rinsing facility) | - personal protective laboratory equipment - laboratory first-aid kit - eye and skin rinsing facilities |
|  |  | Chemical poisoning due to accidental consumption of chemicals | - Keep necessary antidotes ready in separate first aid lit - Train all laboratory staff on first aid measures - Prohibit consumption of any food and drinks in laboratory area (sign board!) - Insist of basic hygiene of all persons engaged in laboratory work |  |
|  |  | Respiratory problems due to inhalation of toxic fumes/gases/vapours | - Install proper fume cabinet or cup board - Provide adequate ventilation of laboratory - Keep oxygen respirator ready | - respirator |
|  |  | Risk of (chemical) fire | - Provide and maintain proper ventilation of laboratory - Keep fire extinguisher (DCP) and sand buckets ready in and outside laboratory room | - fire fighting equipment |
| - 6. | Electrical supply |  |  |  |
| 6.1. | MCC room | Injuries and burns due to electrical fires and explosions | - Regularly check all electrical installations - Provide insulation mats and proper anti-static tools - Provide proper ventilation to dissipate heat from MCC room - Affix “no-smoking sign” in and outside MCC room | - insulation mats - adequate tools |
|  |  | Electrocution | - Work to be carried out only by qualified contractors and workers - Regular checks of installations and equipment - Display first aid measures - Train concerned personnel in electrical safety and emergency measures - Keep rescue equipment and suitable fire fighting equipment readily available | - electrical rescue equipment (pole with hook) |

| Sl. No | Area of operation | Anticipated risk | Recommended OSH practices | Inputs needed |
| --- | --- | --- | --- | --- |
| 6.2. | DG room | Injuries and burns due to explosion and fire | - Ensure DG alternator is covered - Train concerned personnel on electrical safety and emergency aspects including first aid - Display safety card showing name and address of nearest doctor - Ensure proper ventilation of DG room to dissipate fumes and heat - Provide well-maintained fire fighting equipment outside DG room - Install and place proper fuel storage (tank) outside DG room - Affix “no-smoking” sign in and outside DG room | - fire fighting equipment |
| - 6.3. | Electrical installations | Electrocutions, burns | - All installations in the CETP shall comply with IP55 standard. |  |
| 7. | Administration | Fainting due to bad air | - Provide adequate ventilation - Keep offices away from receiving sump of CETP/ETP |  |